## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
2 | 2 | 1.045 | 0 | 0.4 | 0.424 | 0.217 | 0.127 | -0.4 | 0.5 | 1 | 1
3 | 2 | 1.01 | 0 | 0 | 0.234 | 0.942 | 0.19 | 0 | 0.4 | 1 | 1
4 | 3 | 1 | 0 | 0 | 0 | 0.478 | -0.039 | 0 | 0 | 1 | 1
5 | 3 | 1 | 0 | 0 | 0 | 0.076 | 0.016 | 0 | 0 | 1 | 1
6 | 2 | 1.07 | 0 | 0 | 0.122 | 0.112 | 0.075 | -0.06 | 0.24 | 1 | 1
7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
8 | 2 | 1.09 | 0 | 0 | 0.174 | 0 | 0 | -0.06 | 0.24 | 1 | 1
9 | 3 | 1 | 0 | 0 | 0 | 0.295 | 0.166 | 0 | 0 | 1 | 1
10 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.058 | 0 | 0 | 1 | 1
11 | 3 | 1 | 0 | 0 | 0 | 0.035 | 0.018 | 0 | 0 | 1 | 1
12 | 3 | 1 | 0 | 0 | 0 | 0.061 | 0.016 | 0 | 0 | 1 | 1
13 | 3 | 1 | 0 | 0 | 0 | 0.135 | 0.058 | 0 | 0 | 1 | 1
14 | 3 | 1 | 0 | 0 | 0 | 0.149 | 0.05 | 0 | 0 | 1 | 1

## Apparatus
This sheet summarizes the apparatuses connected to buses.
Bus number | Apparatus type | Apparatus parameters
1 | 30 | 1.8 | 0.5 | 0.33 | 1 | 0.95 | 0.45 | 0.2 | 0.02 | 9.32 | 0.05 | 2 | 0.09 | 2.1028 | 1 | 0.103 | 10.6599 | 0.02056 | 200 | 20 | 0 | 2*pi*60
2 | 30 | 1.5 | 0.5 | 0.32 | 1 | 1 | 0.45 | 0.2 | 0.02 | 8.57 | 0.05 | 2 | 0.09 | 2.1028 | 1 | 0.103 | 10.6599 | 0.02056 | 200 | 20 | 0 | 2*pi*60
3 | 30 | 1.8 | 0.5 | 0.33 | 1 | 0.95 | 0.45 | 0.2 | 0.02 | 8.88 | 0.05 | 2 | 0.09 | 2.1028 | 1 | 0.103 | 10.6599 | 0.02056 | 200 | 20 | 0 | 2*pi*60
6 | 30 | 1.5 | 0.5 | 0.32 | 1 | 1 | 0.45 | 0.2 | 0.02 | 8.32 | 0.05 | 2 | 0.09 | 2.1028 | 1 | 0.103 | 10.6599 | 0.02056 | 200 | 20 | 0 | 2*pi*60
8 | 30 | 1.5 | 0.5 | 0.32 | 1 | 1 | 0.45 | 0.2 | 0.02 | 9.21 | 0.05 | 2 | 0.09 | 2.1028 | 1 | 0.103 | 10.6599 | 0.02056 | 200 | 20 | 0 | 2*pi*60

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
1 | 2 | 0.01938 | 0.05917 | 0.0528 | 0 | 1
1 | 5 | 0.05403 | 0.22304 | 0.0492 | 0 | 1
2 | 3 | 0.04699 | 0.19797 | 0.0438 | 0 | 1
2 | 4 | 0.05811 | 0.17632 | 0.034 | 0 | 1
2 | 5 | 0.05695 | 0.17388 | 0.0346 | 0 | 1
3 | 4 | 0.06701 | 0.17103 | 0.0128 | 0 | 1
4 | 5 | 0.01335 | 0.04211 | 0 | 0 | 1
4 | 7 | 0 | 0.20912 | 0 | 0 | 0.978
4 | 9 | 0 | 0.55618 | 0 | 0 | 0.969
5 | 6 | 0 | 0.25202 | 0 | 0 | 0.932
6 | 11 | 0.09498 | 0.1989 | 0 | 0 | 1
6 | 12 | 0.12291 | 0.25581 | 0 | 0 | 1
6 | 13 | 0.06615 | 0.13027 | 0 | 0 | 1
7 | 8 | 0 | 0.17615 | 0 | 0 | 1
7 | 9 | 0 | 0.11001 | 0 | 0 | 1
9 | 10 | 0.03181 | 0.0845 | 0 | 0 | 1
9 | 14 | 0.12711 | 0.27038 | 0 | 0 | 1
10 | 11 | 0.08205 | 0.19207 | 0 | 0 | 1
12 | 13 | 0.22092 | 0.19988 | 0 | 0 | 1
13 | 14 | 0.17093 | 0.34802 | 0 | 0 | 1
9 | 9 | inf | inf | 0.19 | 0 | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 30000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## Advance
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 1
Enable (plot pole map) | 1
Enable (plot admittance) | 1
Enable (print output) | 1
Enable (modal analysis) | 0