## Bus
This sheet summarizes the parameters for power flow analysis
Notes:
Area type: 1-AC, 2-DC.
AC bus type: 1-slack bus, 2-PV bus, 3-PQ bus
DC bus type: 1-slack bus (V bus), 2-N/A, 3-P bus (I bus)
The bus 1 HAVE TO be the slack bus, i.e., type-1 bus.
PGi and QGi are in generator convention. PLi and QLi are in load convention.
For active device (SG, VSI, etc), please use PGi and QGi. For load, please use PLi and QLi.
The load can also be added to network line directly with setting Pli and Qli to zero here.
User data:
Bus No. | Bus type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1 | 0 | 0.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
2 | 2 | 1 | 0 | -0.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
3 | 2 | 1 | 0 | -0.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
4 | 3 | 1 | 0 | -0.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1

## Device
This sheet summarizes the devices connected to buses.
Notes:
For each bus, at least ONE and only ONE device can be connected.
The buses and corresponding devices CAN be listed below in arbitrary order.
The default value will be used if the corresponding customer paramter is left to blank.
The blue highlighted devices are not available currently.
For adding passive load, please use PLi and QLi in the "PowerFlow" sheet.
The dc and ac-dc hybrid devices support default data only, and do not support custormized data for now.
Device type with default values:
| Device type | Default parameters
%===============================
% 0000-0100: AC device
%===============================
%%%
| 0-10: Synchronous machine | H = 3.5 pu | D = 1 pu | wL = 0.1 pu | R = 0.01 pu
0: constant field flux, rotor motion of torque
1: constant flux voltage, rotor motion of power
2: with exitation circuit
3: with prime mover control
%%%
| 10-19: Grid-following inverter with PLL | Vdc = 2.5 pu | Cdc = 1.25 pu | wL = 0.03 pu | R = 0.01 pu | Bandwidth: vdc = 20 Hz | Bandwidth: PLL = 20 Hz | Bandwidth: idq = 500 Hz
10: dc-side input is Pdc
11: fixed vdc, id_r = Pdc/vd
12: dc-side input is idc = Pdc/vdc_r
19: stationary frame modeling
%%%
| 20-29: Grid-forming inverter with frequency droop | wLf = 0.05 pu | Rf = 0.05/5 pu | wCf = 0.02 pu | wLc = 0.01 pu | Rc = 0.01/5 pu | Xov = 0 pu | w droop gain Dw = 5/100 pu | Bandwidth: droop = 20 Hz | Bandwidth: vdq = 250 Hz | Bandwidth: idq = 500 Hz
20: fixed vdc
%%%
| 90: AC infinite bus (short circuit in small-signal) | Note: the voltage and frequency of infinite bus are setted by power flow.
%%%
| 100: AC floating bus (open circuit) | Note: the floating bus is used for the case when "no device" is connected.
%===============================
% 1000-1100: DC device
%===============================
%%%
| 1010-1019: Grid-feeding buck converter | Vdc = 2 pu | Cdc = 0.8 pu | wL = 0.05 pu | R = 0.01 pu | Bandwidth i = 500 Hz | Bandwidth vdc = 10 Hz
1000: fixed vdc
1001: with vdc dynamics
%%%
1020-1029: Grid-forming buck converter
1010: fixed vdc
%%%
1090: DC infinite bus (small-signal short-circuit)
%%%
1100: DC floating bus (open circuit)
%===============================
% 2000-2100: Hybrid device
%===============================
%%%
| 2000-2009: AC-DC interlink converter | Cdc = 1.6 pu | wLac = 0.05 pu | Rac = 0.05/5 | Ldc = 0.01 pu | Rdc = 0.01/5 pu | Bandwidth idq = 500 Hz | Bandwidth vdc = 10 Hz | Bandwidth PLL = 10 Hz
2000: power flow control (grid-feeding at both sides)
2001: vdc control (grid-forming at dc side)
2002: vac control (grid-forming at ac side)
2003: transfverter (grid-forming at both sides)
User data:
Bus No. | Device type | Device parameters
1 | 1 | 3.5 | 10 | 0.05 | 0.01
2 | 1 | 3.5 | 10 | 0.05 | 0.01
3 | 1 | 3.5 | 10 | 0.05 | 0.01
4 | 1 | 3.5 | 10 | 0.05 | 0.01

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Notes:
In this form, a pi-circuit between two buses, i.e., series R+jX impedance with parallel G/2+jB/2 admittance at two terminals.
The transformer is added between FromBus and branch.
The branches can be listed in arbitrary order.
FromBus should NOT equal to ToBus in this list.
For using this sheet, please set enable from 0 to 1, then this sheet will over-write "NetworkLine"
Enable:
0
User data:
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio

## NetworkLine
This sheet summarizes the parameters for network line impedance.
Notes:
In this form, Zbranch = R+jwL+1/(G+jwC)
The transformer is added by turn ratio, which is connected between FromBus and Zbranch in the layout.
The branches can be listed in arbitrary order.
Mutual branch HAS TO be RL.
Self branch HAS TO be GC.
User data:
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)
1 | 2 | 0.05 | 0.5 | 0 | inf | 1
2 | 3 | 0.05 | 0.5 | 0 | inf | 1
3 | 4 | 0.05 | 0.5 | 0 | inf | 1
1 | 1 | 0 | 0 | 0.001 | 0 | 1
2 | 2 | 0 | 0 | 0.001 | 0 | 1
3 | 3 | 0 | 0 | 0.001 | 0 | 1
4 | 4 | 0 | 0 | 0.001 | 0 | 1

## Basic
This sheet summarizes basic settings
User data:
Samping frequency (Hz) | 25000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## Advance
This sheet summaries advanced settings.
Notes:
The Newton-Raphson power flow method can be used for pure ac grids only.
User data:
Item | Value | Notes
Discretization method | 2 | 1-Forward Eular, 2-Hybrid Euler-Trapezoidal
Linearization times | 1 | 1-Initial step, 2-Every step
Discretization damping flag | 1 | 1-With virtual damping resistor, 2-Without virtual damping resistor
Direct feedthrough | 0 | 0-No, 1-Yes
Power flow algorithm | 1 | 1-Gauss-Seidel, 2-Newton-Raphson
Enable (create simulink model) | 0 | 0-Disable, 1-Enable
Enable (plot pole map) | 1 | 0-Disable, 1-Enable
Enable (plot admittance) | 1 | 0-Disable, 1-Enable
Enable (print output) | 1 | 0-Disable, 1-Enable
Enable (participation) | 0 | 0-Disable, 1-Enable