## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
2 | 2 | 1.045 | 0 | 0.4 | 0.424 | 0.217 | 0.127 | -0.4 | 0.5 | 1 | 1
3 | 2 | 1.01 | 0 | 0 | 0.234 | 0.942 | 0.19 | 0 | 0.4 | 1 | 1
4 | 3 | 1 | 0 | 0 | 0 | 0.478 | -0.039 | 0 | 0 | 1 | 1
5 | 3 | 1 | 0 | 0 | 0 | 0.076 | 0.016 | 0 | 0 | 1 | 1
6 | 2 | 1.07 | 0 | 0 | 0.122 | 0.112 | 0.075 | -0.06 | 0.24 | 1 | 1
7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
8 | 2 | 1.09 | 0 | 0 | 0.174 | 0 | 0 | -0.06 | 0.24 | 1 | 1
9 | 3 | 1 | 0 | 0 | 0 | 0.295 | 0.166 | 0 | 0 | 1 | 1
10 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.058 | 0 | 0 | 1 | 1
11 | 3 | 1 | 0 | 0.1 | 0 | 0.105 | 0.018 | 0 | 0 | 1 | 1
12 | 3 | 1 | 0 | 0.1 | 0 | 0.183 | 0.016 | 0 | 0 | 1 | 1
13 | 3 | 1 | 0 | 0.1 | 0 | 0.405 | 0.058 | 0 | 0 | 1 | 1
14 | 3 | 1 | 0 | 0 | 0 | 0.149 | 0.05 | 0 | 0 | 1 | 1

## Apparatus
This sheet summarizes the devices connected to buses.
| 10-19: Grid-following voltage- source inverter with PLL | Vdc (pu) = 2.5 | Cdc (pu) | wL (pu) | R (pu) | Bandwidth vdc (Hz) | Bandwidth PLL (Hz) | Bandwidth idq (Hz) | [24 empty] | PSS-conv | [7 empty] | Governor-BPA_GG
SM Param
|  | Sbase | X | R | x_d | x'd | x''d | T'd | T''d | xq | x'q | x''q | T'q | T''q | H (s) | D (damping torque coefficient, pu) | Dpu (turbine shaft friction torque coefficient, pu) | S(1.0), Machine saturation at 1.0 p.u | S(1.2),Machine saturation at 1.2 p.u. | Tr | Ka | Ta | Vrmax | Vrmin | Ke | Te | Kf | Tf | E1 | SE(E1) | E2 | SE(E2) | T1 | T2 | T3 | T4 | Tw | Kpss | Vpssmin | Vpssmax | R | T1 | T2 | T3 | T4 | T5 | F | Pmax
1 | 42 | 4.48 | 0.15 | 0.0043 | 1.67 | 0.265 | 0.205 | 0.5871 | 0.0248 | 1.6 | 0.46 | 0.205 | 0.1351 | 0.0267 | 2.656 | 1 | 2 | 0.091 | 0.4 | 0 | 50 | 0.06 | 1 | -1 | -0.0465 | 0.52 | 0.0832 | 1 | 3.24 | 0.072 | 4.32 | 0.2821 | 5 | 0.6 | 3 | 0.5 | 10 | 0 | -0.2 | 0.2 | 0.011 | 0 | 0.1 | 0.3 | 0.05 | 10 | 0.25 | 0.87
2 | 42 | 1 | 0.075 | 0.01 | 1.18 | 0.22 | 0.145 | 1.1 | 0.0277 | 1.05 | 0.38 | 0.145 | 0.1086 | 0.0351 | 4.985 | 1 | 2 | 0.0933 | 0.4044 | 0.06 | 25 | 0.2 | 1 | -1 | -0.0582 | 0.6544 | 0.105 | 0.35 | 2.5785 | 0.0889 | 3.438 | 0.3468 | 5 | 0.6 | 3 | 0.5 | 10 | 0 | -0.2 | 0.2 | 0.05 | 0 | 0.09 | 0.2 | 0.3 | 10 | 1 | 1.05
3 | 41 | 0.4 | 0.132 | 0.005 | 2.373 | 0.343 | 0.231 | 11.6 | 0.058 | 1.172 | 1.172 | 0.231 | 0.159 | 0.201 | 1.52 | 0 | 0 | 0.295 | 0.776 | 0 | 400 | 0.05 | 6.63 | -6.63 | -0.17 | 0.95 | 0.04 | 1 | 6.375 | 0.2174 | 8.5 | 0.9388 | 5 | 0.6 | 3 | 0.5 | 10 | 0 | -0.2 | 0.2
4 | 100
5 | 100
6 | 41 | 0.25 | 0.1045 | 0.0025 | 1.769 | 0.304 | 0.2035 | 8 | 0.0525 | 0.855 | 0.5795 | 0.2035 | 0.008 | 0.0151 | 1.2 | 1 | 0 | 0.304 | 0.666 | 0 | 400 | 0.05 | 4.407 | -4.407 | -0.17 | 0.95 | 0.04 | 1 | 4.2375 | 0.2174 | 5.65 | 0.9386
7 | 100
8 | 41 | 0.25 | 0.1045 | 0.0025 | 1.769 | 0.304 | 0.2035 | 8 | 0.0525 | 0.855 | 0.5795 | 0.2035 | 0.008 | 0.0151 | 1.2 | 0 | 0 | 0.304 | 0.666 | 0 | 400 | 0.05 | 4.407 | -4.407 | -0.17 | 0.95 | 0.04 | 1 | 4.2375 | 0.2174 | 5.65 | 0.9386
9 | 100
10 | 100
11 | 10 | 2.5 | 1.25 | 0.025 | 0.001 | 10 | 20 | 450
12 | 10 | 2.5 | 1.25 | 0.025 | 0.001 | 10 | 30 | 320
13 | 10 | 2.5 | 1.25 | 0.025 | 0.001 | 10 | 20 | 450
14 | 100
Note on AQ4: Zhu, Yue: T1 and T2 are inverted in Cyprus's model, so I changed them back.

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 25000
Base frequency (Hz) | 50
Base power (VA) | 1
Base voltage (V) | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
1 | 2 | 0.01938 | 0.05917 | 0.0528 | 0 | 1
1 | 5 | 0.05403 | 0.22304 | 0.0492 | 0 | 1
2 | 3 | 0.04699 | 0.19797 | 0.0438 | 0 | 1
2 | 4 | 0.05811 | 0.17632 | 0.034 | 0 | 1
2 | 5 | 0.05695 | 0.17388 | 0.0346 | 0 | 1
3 | 4 | 0.06701 | 0.17103 | 0.0128 | 0 | 1
4 | 5 | 0.01335 | 0.04211 | 1e-07 | 0 | 1
4 | 7 | 1e-07 | 0.20912 | 1e-07 | 0 | 0.978
4 | 9 | 1e-07 | 0.55618 | 1e-07 | 0 | 0.969
5 | 6 | 1e-07 | 0.25202 | 1e-07 | 0 | 0.932
6 | 11 | 0.09498 | 0.1989 | 1e-07 | 0 | 1
6 | 12 | 0.12291 | 0.25581 | 1e-07 | 0 | 1
6 | 13 | 0.06615 | 0.13027 | 1e-07 | 0 | 1
7 | 8 | 1e-07 | 0.17615 | 1e-07 | 0 | 1
7 | 9 | 1e-07 | 0.11001 | 1e-07 | 0 | 1
9 | 10 | 0.03181 | 0.0845 | 1e-07 | 0 | 1
9 | 14 | 0.12711 | 0.27038 | 1e-07 | 0 | 1
10 | 11 | 0.08205 | 0.19207 | 1e-07 | 0 | 1
12 | 13 | 0.22092 | 0.19988 | 1e-07 | 0 | 1
13 | 14 | 0.17093 | 0.34802 | 1e-07 | 0 | 1
9 | 9 | inf | inf | 0.19 | 0 | 1

## Advance
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 0
Enable (plot pole map) | 1
Enable (plot admittance) | 0
Enable (print output) | 1
Enable (modal analysis) | 0