## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 0.966 | 0 | 0 | 0 | 6.048 | -0.196 | -10 | 10 | 1 | 1
2 | 2 | 1.039 | 0 | 6.5 | 1.9586 | 0.0626 | 0.0243 | -10 | 10 | 1 | 1
3 | 2 | 0.989 | 0 | 0.5 | 0 | 0.0798 | 0.0798 | -10 | 10 | 1 | 1
4 | 2 | 0.998 | 0 | 2 | -1.06 | 3.79 | -0.886 | -10 | 10 | 1 | 1
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 0.0049

## Apparatus
This sheet summarizes the devices connected to buses.
| 10-19: Grid-following voltage- source inverter with PLL | Vdc (pu) = 2.5 | Cdc (pu) | wL (pu) | R (pu) | Bandwidth vdc (Hz) | Bandwidth PLL (Hz) | Bandwidth idq (Hz) | [24 empty] | PSS-conv | [7 empty] | Governor-BPA_GG
| GFM inverter | wLf (pu) | Rf (pu) | wCf (pu) | wLc (pu) | Rc (pu) | Xov (pu) | Droop Dw | BW droop (Hz) | BW vdq (Hz) | BW idq (Hz)
SM Param
| SG | Sbase | X | R | x_d | x'd | x''d | T'd | T''d | xq | x'q | x''q | T'q | T''q | H (s) | D (damping torque coefficient, pu) | Dpu (turbine shaft friction torque coefficient, pu) | S(1.0), Machine saturation at 1.0 p.u | S(1.2),Machine saturation at 1.2 p.u. | Tr | Ka | Ta | Vrmax | Vrmin | Ke | Te | Kf | Tf | E1 | SE(E1) | E2 | SE(E2) | T1 | T2 | T3 | T4 | Tw | Kpss | Vpssmin | Vpssmax | R | T1 | T2 | T3 | T4 | T5 | F | Pmax
1 | 42 | 4.48 | 0.15 | 0.0043 | 2 | 0.265 | 0.205 | 0.5871 | 0.0248 | 1.6 | 0.46 | 0.205 | 0.1351 | 0.0267 | 2.656 | 0 | 2 | 0.091 | 0.4 | 0 | 50 | 0.06 | 1 | -1 | -0.0465 | 0.52 | 0.12 | 1 | 3.24 | 0.072 | 4.32 | 0.2821 | 5 | 0.6 | 3 | 0.5 | 10 | 0 | -0.2 | 0.2 | 0.011 | 0 | 0.1 | 0.3 | 0.05 | 10 | 0.25 | 0.87
2 | 20 | 0.01 | 0.002 | 0.1 | 0.002 | 0.0005 | 0.002 | 0.03 | 5 | 300 | 600
3 | 42 | 0.8 | 0.15 | 0.0043 | 2 | 0.265 | 0.205 | 0.5871 | 0.0248 | 1.6 | 0.46 | 0.205 | 0.1351 | 0.0267 | 2.656 | 0 | 2 | 0.091 | 0.4 | 0 | 50 | 0.06 | 1 | -1 | -0.0465 | 0.52 | 0.12 | 1 | 3.24 | 0.072 | 4.32 | 0.2821 | 5 | 0.6 | 3 | 0.5 | 10 | 0 | -0.2 | 0.2 | 0.011 | 0 | 0.1 | 0.3 | 0.05 | 10 | 0.25 | 0.87
4 | 20 | 0.01 | 0.002 | 0.1 | 0.002 | 0.0005 | 0.002 | 0.03 | 5 | 300 | 600
Note on AQ5: Zhu, Yue: T1 and T2 are inverted in Cyprus's model, so I changed them back.
Note on F6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 1.67
Note on F8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Was 1.67

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 30000
Base frequency (Hz) | 60
Base power (VA) | 1000000000
Base voltage (V) | 100000

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
1 | 3 | 0.004 | 0.057 | 1e-09 | 0 | 1
2 | 3 | 0.0029 | 0.0734 | 1e-09 | 0 | 1
3 | 4 | 0 | 0.039 | 1e-09 | 0 | 1
1 | 1 | inf | inf | 0.042 | 1e-05 | 1
2 | 2 | inf | inf | 0.0368 | 1e-05 | 1
3 | 3 | inf | inf | 2.142 | 1e-05 | 1
4 | 4 | inf | inf | 0.033 | 1e-05 | 1

## Advance
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 1
Enable (plot pole map) | 1
Enable (plot admittance) | 0
Enable (print output) | 1
Enable (modal analysis) | 0