## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1 | 0 | 40 | 0 | 0 | 0 | -999 | 999 | 1 | 1
2 | 2 | 0.98 | 0 | 3.45 | 0 | 0 | 0 | -999 | 999 | 1 | 1
3 | 2 | 0.983 | 0 | 6.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
4 | 2 | 0.997 | 0 | 6.32 | 0 | 0 | 0 | -999 | 999 | 1 | 1
5 | 2 | 1.011 | 0 | 5.05 | 0 | 0 | 0 | -999 | 999 | 1 | 1
6 | 2 | 1.05 | 0 | 7 | 0 | 0 | 0 | -999 | 999 | 1 | 1
7 | 2 | 1.063 | 0 | 5.6 | 0 | 0 | 0 | -999 | 999 | 1 | 1
8 | 2 | 1.03 | 0 | 5.4 | 0 | 0 | 0 | -999 | 999 | 1 | 1
9 | 2 | 1.025 | 0 | 2 | 0 | 0 | 0 | -999 | 999 | 1 | 1
10 | 2 | 1.01 | 0 | 5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
11 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999 | 1 | 1
12 | 2 | 1.0156 | 0 | 13.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
13 | 2 | 1.011 | 0 | 31.91 | 0 | 0 | 0 | -999 | 999 | 1 | 1
14 | 2 | 1 | 0 | 17.85 | 0 | 0 | 0 | -999 | 999 | 1 | 1
15 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999 | 1 | 1
16 | 2 | 1.045 | 0 | 2.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
17 | 3 | 1 | 0 | 4 | 0 | 60 | 3 | 0 | 0 | 1 | 1
18 | 3 | 1 | 0 | 0 | 0 | 24.7 | 1.23 | 0 | 0 | 1 | 1
19 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
20 | 3 | 1 | 0 | 0 | 0 | 6.8 | 1.03 | 0 | 0 | 1 | 1
21 | 3 | 1 | 0 | 0 | 0 | 2.74 | 1.15 | 0 | 0 | 1 | 1
22 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
23 | 3 | 1 | 0 | 0 | 0 | 2.48 | 0.85 | 0 | 0 | 1 | 1
24 | 3 | 1 | 0 | 0 | 0 | 3.09 | -0.92 | 0 | 0 | 1 | 1
25 | 3 | 1 | 0 | 0 | 0 | 2.24 | 0.47 | 0 | 0 | 1 | 1
26 | 3 | 1 | 0 | 2 | 0 | 1.39 | 0.17 | 0 | 0 | 1 | 1
27 | 3 | 1 | 0 | 0 | 0 | 2.81 | 0.76 | 0 | 0 | 1 | 1
28 | 3 | 1 | 0 | 2 | 0 | 2.06 | 0.28 | 0 | 0 | 1 | 1
29 | 3 | 1 | 0 | 2 | 0 | 2.84 | 0.27 | 0 | 0 | 1 | 1
30 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
31 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
32 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
33 | 3 | 1 | 0 | 0 | 0 | 1.12 | 0 | 0 | 0 | 1 | 1
34 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
35 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
36 | 3 | 1 | 0 | 0 | 0 | 1.02 | -0.1946 | 0 | 0 | 1 | 1
37 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
38 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
39 | 3 | 1 | 0 | 0 | 0 | 2.67 | 0.126 | 0 | 0 | 1 | 1
40 | 3 | 1 | 0 | 0 | 0 | 0.6563 | 0.2353 | 0 | 0 | 1 | 1
41 | 3 | 1 | 0 | 0 | 0 | 10 | 2.5 | 0 | 0 | 1 | 1
42 | 3 | 1 | 0 | 0 | 0 | 11.5 | 2.5 | 0 | 0 | 1 | 1
43 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
44 | 3 | 1 | 0 | 0 | 0 | 2.6755 | 0.0484 | 0 | 0 | 1 | 1
45 | 3 | 1 | 0 | 0 | 0 | 2.08 | 0.21 | 0 | 0 | 1 | 1
46 | 3 | 1 | 0 | 0 | 0 | 1.507 | 0.285 | 0 | 0 | 1 | 1
47 | 3 | 1 | 0 | 0 | 0 | 2.0312 | 0.3259 | 0 | 0 | 1 | 1
48 | 3 | 1 | 0 | 0 | 0 | 2.412 | 0.022 | 0 | 0 | 1 | 1
49 | 3 | 1 | 0 | 0 | 0 | 1.64 | 0.29 | 0 | 0 | 1 | 1
50 | 3 | 1 | 0 | 0 | 0 | 1 | -1.47 | 0 | 0 | 1 | 1
51 | 3 | 1 | 0 | 0 | 0 | 3.37 | -1.22 | 0 | 0 | 1 | 1
52 | 3 | 1 | 0 | 0 | 0 | 1.58 | 0.3 | 0 | 0 | 1 | 1
53 | 3 | 1 | 0 | 0 | 0 | 2.527 | 1.1856 | 0 | 0 | 1 | 1
54 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
55 | 3 | 1 | 0 | 0 | 0 | 3.22 | 0.02 | 0 | 0 | 1 | 1
56 | 3 | 1 | 0 | 0 | 0 | 2 | 0.736 | 0 | 0 | 1 | 1
57 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
58 | 3 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1
59 | 3 | 1 | 0 | 1 | 0 | 2.34 | 0.84 | 0 | 0 | 1 | 1
60 | 3 | 1 | 0 | 0 | 0 | 2.088 | 0.708 | 0 | 0 | 1 | 1
61 | 3 | 1 | 0 | 0 | 0 | 1.04 | 1.25 | 0 | 0 | 1 | 1
62 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
63 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
64 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.88 | 0 | 0 | 1 | 1
65 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
66 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
67 | 3 | 1 | 0 | 0 | 0 | 3.2 | 1.53 | 0 | 0 | 1 | 1
68 | 3 | 1 | 0 | 0 | 0 | 3.29 | 0.32 | 0 | 0 | 1 | 1

## Apparatus
This sheet summarizes the devices connected to buses.
|  | SM | [13 empty] | EXCITER | [16 empty] | PSS
|  | X | R | x_d | x'd | x''d | T'd | T''d | xq | x'q | x''q | T'q | T''q | H | D | input filter time constant T_R | voltage regulator gain K_A | voltage regulator time constant T_A | maximum voltage regulator output V_Rmax | minimum voltage regulator output V_Rmin | exciter constant K_E | exciter time constant T_E | E_1 | S(E_1) | E_2 | S(E_2) | stabilizer gain K_F | stabilizer time constant T_F | K_P | K_I | K_D | T_D | KPSS | TW | T11 | T12 | T21 | T22 | T31 | T32 | VSSmax | VSSmin
1 | 38 | 0.00205 | 0.0041 | 0.0178 | 0.00355 | 0.00275 | 7.8 | 0.05 | 0.0167 | 0.00475 | 0.00275 | 1.5 | 0.035 | 450 | 0
2 | 39 | 0.035 | 0.07 | 0.295 | 0.0697 | 0.05 | 6.56 | 0.05 | 0.282 | 0.093333 | 0.05 | 1.5 | 0.035 | 30.2 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
3 | 39 | 0.0304 | 0.0608 | 0.2495 | 0.0531 | 0.045 | 5.7 | 0.05 | 0.237 | 0.071429 | 0.045 | 1.5 | 0.035 | 35.8 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
4 | 39 | 0.0295 | 0.059 | 0.262 | 0.0436 | 0.035 | 5.69 | 0.05 | 0.258 | 0.058571 | 0.035 | 1.5 | 0.035 | 28.6 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
5 | 39 | 0.027 | 0.054 | 0.33 | 0.066 | 0.05 | 5.4 | 0.05 | 0.31 | 0.088333 | 0.05 | 0.44 | 0.035 | 26 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
6 | 39 | 0.0224 | 0.0448 | 0.254 | 0.05 | 0.04 | 7.3 | 0.05 | 0.241 | 0.0675 | 0.04 | 0.4 | 0.035 | 34.8 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
7 | 39 | 0.0322 | 0.0644 | 0.295 | 0.049 | 0.04 | 5.66 | 0.05 | 0.292 | 0.066667 | 0.04 | 1.5 | 0.035 | 26.4 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
8 | 39 | 0.028 | 0.056 | 0.29 | 0.057 | 0.045 | 6.7 | 0.05 | 0.28 | 0.076667 | 0.045 | 0.41 | 0.035 | 24.3 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
9 | 39 | 0.0298 | 0.0596 | 0.2106 | 0.057 | 0.045 | 4.79 | 0.05 | 0.205 | 0.076667 | 0.045 | 1.96 | 0.035 | 34.5 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
10 | 39 | 0.0199 | 0.0398 | 0.169 | 0.0457 | 0.04 | 9.37 | 0.05 | 0.115 | 0.061539 | 0.04 | 1.5 | 0.035 | 31 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
11 | 39 | 0.0103 | 0.0206 | 0.128 | 0.018 | 0.012 | 4.1 | 0.05 | 0.123 | 0.024118 | 0.012 | 1.5 | 0.035 | 28.2 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
12 | 39 | 0.022 | 0.044 | 0.101 | 0.031 | 0.025 | 7.4 | 0.05 | 0.095 | 0.042 | 0.025 | 1.5 | 0.035 | 92.3 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
13 | 38 | 0.0015 | 0.003 | 0.0148 | 0.00275 | 0.002 | 5.9 | 0.05 | 0.0143 | 0.0037 | 0.002 | 1.5 | 0.035 | 496 | 0
14 | 38 | 0.0017 | 0.0034 | 0.018 | 0.00285 | 0.0023 | 4.1 | 0.05 | 0.0173 | 0.0037931 | 0.0023 | 1.5 | 0.035 | 300 | 0
15 | 21 | 0.2 | 0.02 | 0.08 | 0.03 | 9.55e-06 | 0 | 0.0045 | 20 | 100 | 250
16 | 39 | 0.0125 | 0.025 | 0.1 | 0.031 | 0.025 | 10.2 | 0.05 | 0.069 | 0.041667 | 0.025 | 1.5 | 0.035 | 42 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
17 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
18 | 100
19 | 100
20 | 100
21 | 100
22 | 100
23 | 100
24 | 100
25 | 100
26 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
27 | 100
28 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 300
29 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 220
30 | 100
31 | 100
32 | 100
33 | 100
34 | 100
35 | 100
36 | 100
37 | 100
38 | 100
39 | 100
40 | 100
41 | 100
42 | 100
43 | 100
44 | 100
45 | 100
46 | 100
47 | 100
48 | 100
49 | 100
50 | 100
51 | 100
52 | 100
53 | 100
54 | 100
55 | 100
56 | 100
57 | 100
58 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
59 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
60 | 100
61 | 100
62 | 100
63 | 100
64 | 100
65 | 100
66 | 100
67 | 100
68 | 100
Note on A4: Yue Zhu: Bus 1 and Bus 16 are swapt here because in the Toolbox, bus 1 has to be the swing bus. In the results of the paper, they are swapt back.
Note on AB14: Zhu, Yue: The parameters of A11 are kept the same as the original model, but seems to be quite different compared with other nearby machine. And it is reported that A11 is considered as an unstable machine in this 68 bus system.
Note on C16: Yue Zhu: The power rating of M1 (original M16) and M13 are 2 times of others, therefore the parameters should be changed: X becomes 1/2 of the orignal, D and H becomes 2 times.
Note on I18: Yue Zhu: Deliberately detuned high.
Note on I32: Yue Zhu: deliberately detuned low.

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 30000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
16 | 54 | 1e-07 | 0.0181 | 0 | 0 | 1.025
2 | 58 | 1e-07 | 0.025 | 0 | 0 | 1.07
3 | 62 | 1e-07 | 0.02 | 0 | 0 | 1.07
4 | 19 | 0.0007 | 0.0142 | 0 | 0 | 1.07
5 | 20 | 0.0009 | 0.018 | 0 | 0 | 1.009
6 | 22 | 1e-07 | 0.0143 | 0 | 0 | 1.025
7 | 23 | 0.0005 | 0.0272 | 0 | 0 | 1
8 | 25 | 0.0006 | 0.0232 | 0 | 0 | 1.025
9 | 29 | 0.0008 | 0.0156 | 0 | 0 | 1.025
10 | 31 | 1e-07 | 0.026 | 0 | 0 | 1.04
11 | 32 | 1e-07 | 0.013 | 0 | 0 | 1.04
12 | 36 | 1e-07 | 0.0075 | 0 | 0 | 1.04
13 | 17 | 1e-07 | 0.0033 | 0 | 0 | 1.04
14 | 41 | 1e-07 | 0.0015 | 0 | 0 | 1
15 | 42 | 1e-07 | 0.0015 | 0 | 0 | 1
1 | 18 | 1e-07 | 0.003 | 0 | 0 | 1
17 | 36 | 0.0005 | 0.0045 | 0.32 | 0 | 1
18 | 49 | 0.0076 | 0.1141 | 1.16 | 0 | 1
18 | 50 | 0.0012 | 0.0288 | 2.06 | 0 | 1
19 | 68 | 0.0016 | 0.0195 | 0.304 | 0 | 1
20 | 19 | 0.0007 | 0.0138 | 0 | 0 | 1.06
21 | 68 | 0.0008 | 0.0135 | 0.2548 | 0 | 1
22 | 21 | 0.0008 | 0.014 | 0.2565 | 0 | 1
23 | 22 | 0.0006 | 0.0096 | 0.1846 | 0 | 1
24 | 23 | 0.0022 | 0.035 | 0.361 | 0 | 1
24 | 68 | 0.0003 | 0.0059 | 0.068 | 0 | 1
25 | 54 | 0.007 | 0.0086 | 0.146 | 0 | 1
26 | 25 | 0.0032 | 0.0323 | 0.531 | 0 | 1
27 | 37 | 0.0013 | 0.0173 | 0.3216 | 0 | 1
27 | 26 | 0.0014 | 0.0147 | 0.2396 | 0 | 1
28 | 26 | 0.0043 | 0.0474 | 0.7802 | 0 | 1
29 | 26 | 0.0057 | 0.0625 | 1.029 | 0 | 1
29 | 28 | 0.0014 | 0.0151 | 0.249 | 0 | 1
30 | 53 | 0.0008 | 0.0074 | 0.48 | 0 | 1
30 | 61 | 0.00095 | 0.00915 | 0.58 | 0 | 1
31 | 30 | 0.0013 | 0.0187 | 0.333 | 0 | 1
31 | 53 | 0.0016 | 0.0163 | 0.25 | 0 | 1
32 | 30 | 0.0024 | 0.0288 | 0.488 | 0 | 1
33 | 32 | 0.0008 | 0.0099 | 0.168 | 0 | 1
34 | 33 | 0.0011 | 0.0157 | 0.202 | 0 | 1
34 | 35 | 0.0001 | 0.0074 | 0 | 0 | 0.946
36 | 34 | 0.0033 | 0.0111 | 1.45 | 0 | 1
36 | 61 | 0.0011 | 0.0098 | 0.68 | 0 | 1
37 | 68 | 0.0007 | 0.0089 | 0.1342 | 0 | 1
38 | 31 | 0.0011 | 0.0147 | 0.247 | 0 | 1
38 | 33 | 0.0036 | 0.0444 | 0.693 | 0 | 1
40 | 41 | 0.006 | 0.084 | 3.15 | 0 | 1
40 | 48 | 0.002 | 0.022 | 1.28 | 0 | 1
41 | 42 | 0.004 | 0.06 | 2.25 | 0 | 1
42 | 18 | 0.004 | 0.06 | 2.25 | 0 | 1
43 | 17 | 0.0005 | 0.0276 | 0 | 0 | 1
44 | 39 | 1e-07 | 0.0411 | 0 | 0 | 1
44 | 43 | 0.0001 | 0.0011 | 0 | 0 | 1
45 | 35 | 0.0007 | 0.0175 | 1.39 | 0 | 1
45 | 39 | 1e-07 | 0.0839 | 0 | 0 | 1
45 | 44 | 0.0025 | 0.073 | 0 | 0 | 1
46 | 38 | 0.0022 | 0.0284 | 0.43 | 0 | 1
47 | 53 | 0.0013 | 0.0188 | 1.31 | 0 | 1
48 | 47 | 0.00125 | 0.0134 | 0.8 | 0 | 1
49 | 46 | 0.0018 | 0.0274 | 0.27 | 0 | 1
51 | 45 | 0.0004 | 0.0105 | 0.72 | 0 | 1
51 | 50 | 0.0009 | 0.0221 | 1.62 | 0 | 1
52 | 37 | 0.0007 | 0.0082 | 0.1319 | 0 | 1
52 | 55 | 0.0011 | 0.0133 | 0.2138 | 0 | 1
54 | 53 | 0.0035 | 0.0411 | 0.6987 | 0 | 1
55 | 54 | 0.0013 | 0.0151 | 0.2572 | 0 | 1
56 | 55 | 0.0013 | 0.0213 | 0.2214 | 0 | 1
57 | 56 | 0.0008 | 0.0128 | 0.1342 | 0 | 1
58 | 57 | 0.0002 | 0.0026 | 0.0434 | 0 | 1
59 | 58 | 0.0006 | 0.0092 | 0.113 | 0 | 1
60 | 57 | 0.0008 | 0.0112 | 0.1476 | 0 | 1
60 | 59 | 0.0004 | 0.0046 | 0.078 | 0 | 1
61 | 60 | 0.0023 | 0.0363 | 0.3804 | 0 | 1
63 | 58 | 0.0007 | 0.0082 | 0.1389 | 0 | 1
63 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
63 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
65 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
65 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
66 | 56 | 0.0008 | 0.0129 | 0.1382 | 0 | 1
66 | 65 | 0.0009 | 0.0101 | 0.1723 | 0 | 1
67 | 66 | 0.0018 | 0.0217 | 0.366 | 0 | 1
68 | 67 | 0.0009 | 0.0094 | 0.171 | 0 | 1
27 | 53 | 0.032 | 0.32 | 0.41 | 0 | 1

## Advance
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 0
Enable (plot pole map) | 1
Enable (plot admittance) | 0
Enable (print output) | 1
Enable (modal analysis) | 0