## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1 | 0 | 40 | 0 | 0 | 0 | -999 | 999 | 1 | 1
2 | 2 | 0.98 | 0 | 3.45 | 0 | 0 | 0 | -999 | 999 | 1 | 1
3 | 2 | 0.983 | 0 | 6.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
4 | 2 | 0.997 | 0 | 6.32 | 0 | 0 | 0 | -999 | 999 | 1 | 1
5 | 2 | 1.011 | 0 | 5.05 | 0 | 0 | 0 | -999 | 999 | 1 | 1
6 | 2 | 1.05 | 0 | 7 | 0 | 0 | 0 | -999 | 999 | 1 | 1
7 | 2 | 1.063 | 0 | 5.6 | 0 | 0 | 0 | -999 | 999 | 1 | 1
8 | 2 | 1.03 | 0 | 5.4 | 0 | 0 | 0 | -999 | 999 | 1 | 1
9 | 2 | 1.025 | 0 | 2 | 0 | 0 | 0 | -999 | 999 | 1 | 1
10 | 2 | 1.01 | 0 | 5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
11 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999 | 1 | 1
12 | 3 | 1 | 0 | 5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
13 | 2 | 1.011 | 0 | 11.91 | 0 | 0 | 0 | -999 | 999 | 1 | 1
14 | 2 | 1 | 0 | 17.85 | 0 | 0 | 0 | -999 | 999 | 1 | 1
15 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999 | 1 | 1
16 | 2 | 1.045 | 0 | 2.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
17 | 3 | 1 | 0 | 4 | 0 | 60 | 3 | 0 | 0 | 1 | 1
18 | 3 | 1 | 0 | 0 | 0 | 24.7 | 1.23 | 0 | 0 | 1 | 1
19 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
20 | 3 | 1 | 0 | 0 | 0 | 6.8 | 1.03 | 0 | 0 | 1 | 1
21 | 3 | 1 | 0 | 0 | 0 | 2.74 | 1.15 | 0 | 0 | 1 | 1
22 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
23 | 3 | 1 | 0 | 0 | 0 | 2.48 | 0.85 | 0 | 0 | 1 | 1
24 | 3 | 1 | 0 | 0 | 0 | 3.09 | -0.92 | 0 | 0 | 1 | 1
25 | 3 | 1 | 0 | 0 | 0 | 2.24 | 0.47 | 0 | 0 | 1 | 1
26 | 3 | 1 | 0 | 6 | 0 | 1.39 | 0.17 | 0 | 0 | 1 | 1
27 | 3 | 1 | 0 | 6 | 0 | 2.81 | 0.76 | 0 | 0 | 1 | 1
28 | 3 | 1 | 0 | 6 | 0 | 2.06 | 0.28 | 0 | 0 | 1 | 1
29 | 3 | 1 | 0 | 6 | 0 | 2.84 | 0.27 | 0 | 0 | 1 | 1
30 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
31 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
32 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
33 | 3 | 1 | 0 | 0 | 0 | 1.12 | 0 | 0 | 0 | 1 | 1
34 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
35 | 3 | 1 | 0 | 2 | 0.2 | 0 | 0 | 0 | 0 | 1 | 1
36 | 3 | 1 | 0 | 0 | 0 | 1.02 | -0.1946 | 0 | 0 | 1 | 1
37 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
38 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
39 | 3 | 1 | 0 | 5 | 1 | 2.67 | 0.126 | 0 | 0 | 1 | 1
40 | 3 | 1 | 0 | 0 | 0 | 0.6563 | 0.2353 | 0 | 0 | 1 | 1
41 | 3 | 1 | 0 | 0 | 0 | 10 | 2.5 | 0 | 0 | 1 | 1
42 | 3 | 1 | 0 | 0 | 0 | 11.5 | 2.5 | 0 | 0 | 1 | 1
43 | 3 | 1 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 1 | 1
44 | 3 | 1 | 0 | 5 | 1 | 2.6755 | 0.0484 | 0 | 0 | 1 | 1
45 | 3 | 1 | 0 | 3 | 0.3 | 2.08 | 0.21 | 0 | 0 | 1 | 1
46 | 3 | 1 | 0 | 0 | 0 | 1.507 | 0.285 | 0 | 0 | 1 | 1
47 | 3 | 1 | 0 | 0 | 0 | 2.0312 | 0.3259 | 0 | 0 | 1 | 1
48 | 3 | 1 | 0 | 0 | 0 | 2.412 | 0.022 | 0 | 0 | 1 | 1
49 | 3 | 1 | 0 | 0 | 0 | 1.64 | 0.29 | 0 | 0 | 1 | 1
50 | 3 | 1 | 0 | 4 | 0.4 | 1 | -1.47 | 0 | 0 | 1 | 1
51 | 3 | 1 | 0 | 4 | 0.4 | 3.37 | -1.22 | 0 | 0 | 1 | 1
52 | 3 | 1 | 0 | 0 | 0 | 1.58 | 0.3 | 0 | 0 | 1 | 1
53 | 3 | 1 | 0 | 0 | 0 | 2.527 | 1.1856 | 0 | 0 | 1 | 1
54 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
55 | 3 | 1 | 0 | 0 | 0 | 3.22 | 0.02 | 0 | 0 | 1 | 1
56 | 3 | 1 | 0 | 0 | 0 | 2 | 0.736 | 0 | 0 | 1 | 1
57 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
58 | 3 | 1 | 0 | 1 | 0.1 | 0 | 0 | 0 | 0 | 1 | 1
59 | 3 | 1 | 0 | 1 | 0.1 | 2.34 | 0.84 | 0 | 0 | 1 | 1
60 | 3 | 1 | 0 | 0 | 0 | 2.088 | 0.708 | 0 | 0 | 1 | 1
61 | 3 | 1 | 0 | 0 | 0 | 1.04 | 1.25 | 0 | 0 | 1 | 1
62 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
63 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
64 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.88 | 0 | 0 | 1 | 1
65 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
66 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
67 | 3 | 1 | 0 | 0 | 0 | 3.2 | 1.53 | 0 | 0 | 1 | 1
68 | 3 | 1 | 0 | 0 | 0 | 3.29 | 0.32 | 0 | 0 | 1 | 1
Note on E15: Zhu, Yue: original value: 31.91
Note on G35: Zhu, Yue:

## Apparatus
This sheet summarizes the devices connected to buses.
[16 empty] | EXCITER | [16 empty] | PSS
| SM | X | R | x_d | x'd | x''d | T'd | T''d | xq | x'q | x''q | T'q | T''q | H | D | input filter time constant T_R | voltage regulator gain K_A | voltage regulator time constant T_A | maximum voltage regulator output V_Rmax | minimum voltage regulator output V_Rmin | exciter constant K_E | exciter time constant T_E | E_1 | S(E_1) | E_2 | S(E_2) | stabilizer gain K_F | stabilizer time constant T_F | K_P | K_I | K_D | T_D | KPSS | TW | T11 | T12 | T21 | T22 | T31 | T32 | VSSmax | VSSmin
| GFM | wLf | Rf | wCf | wLc | Rc | Xov | Dw | fdroop | fvdq | fidq | Sbase
| GFL | V_dc | C_dc | wLf | R | f_v_dc | f_pll | f_i_dq | Sbase
1 | 33 | 0.00205 | 0 | 0.0178 | 0.00355 | 0.00275 | 7.8 | 0.05 | 0.0167 | 0.00475 | 0.00275 | 1.5 | 0.035 | 450 | 0
2 | 35 | 0.035 | 0 | 0.295 | 0.0697 | 0.05 | 6.56 | 0.05 | 0.282 | 0.093333 | 0.05 | 1.5 | 0.035 | 30.2 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
3 | 35 | 0.0304 | 0 | 0.2495 | 0.0531 | 0.045 | 5.7 | 0.05 | 0.237 | 0.071429 | 0.045 | 1.5 | 0.035 | 35.8 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
4 | 35 | 0.0295 | 0 | 0.262 | 0.0436 | 0.035 | 5.69 | 0.05 | 0.258 | 0.058571 | 0.035 | 1.5 | 0.035 | 28.6 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
5 | 35 | 0.027 | 0 | 0.33 | 0.066 | 0.05 | 5.4 | 0.05 | 0.31 | 0.088333 | 0.05 | 0.44 | 0.035 | 26 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
6 | 35 | 0.0224 | 0 | 0.254 | 0.05 | 0.04 | 7.3 | 0.05 | 0.241 | 0.0675 | 0.04 | 0.4 | 0.035 | 34.8 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
7 | 35 | 0.0322 | 0 | 0.295 | 0.049 | 0.04 | 5.66 | 0.05 | 0.292 | 0.066667 | 0.04 | 1.5 | 0.035 | 26.4 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
8 | 35 | 0.028 | 0 | 0.29 | 0.057 | 0.045 | 6.7 | 0.05 | 0.28 | 0.076667 | 0.045 | 0.41 | 0.035 | 24.3 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
9 | 35 | 0.0298 | 0 | 0.2106 | 0.057 | 0.045 | 4.79 | 0.05 | 0.205 | 0.076667 | 0.045 | 1.96 | 0.035 | 34.5 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
10 | 35 | 0.0199 | 0 | 0.169 | 0.0457 | 0.04 | 9.37 | 0.05 | 0.115 | 0.061539 | 0.04 | 1.5 | 0.035 | 31 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
11 | 35 | 0.0103 | 0 | 0.128 | 0.018 | 0.012 | 4.1 | 0.05 | 0.123 | 0.024118 | 0.012 | 1.5 | 0.035 | 28.2 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
12 | 35 | 0.022 | 0 | 0.101 | 0.031 | 0.025 | 7.4 | 0.05 | 0.095 | 0.042 | 0.025 | 1.5 | 0.035 | 92.3 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
13 | 33 | 0.0015 | 0 | 0.0148 | 0.00275 | 0.002 | 5.9 | 0.05 | 0.0143 | 0.0037 | 0.002 | 1.5 | 0.035 | 496 | 0
14 | 33 | 0.0017 | 0 | 0.018 | 0.00285 | 0.0023 | 4.1 | 0.05 | 0.0173 | 0.0037931 | 0.0023 | 1.5 | 0.035 | 300 | 0
15 | 33 | 0.0017 | 0 | 0.018 | 0.00285 | 0.0023 | 4.1 | 0.05 | 0.0173 | 0.0037931 | 0.0023 | 1.5 | 0.035 | 300 | 0
16 | 35 | 0.0125 | 0 | 0.1 | 0.031 | 0.025 | 10.2 | 0.05 | 0.069 | 0.041667 | 0.025 | 1.5 | 0.035 | 42 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
17 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
18 | GFM: 100
19 | GFM: 100
20 | GFM: 100
21 | GFM: 100
22 | GFM: 100
23 | GFM: 100
24 | GFM: 100
25 | GFM: 100
26 | 28 | 0.2 | 0.02 | 0.08 | 0.03 | 9.55e-06 | 0 | 0.001 | 10 | 100 | 150 | 6
27 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 10 | 20 | 1000 | 6
28 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 10 | 20 | 1000 | 6
29 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 10 | 20 | 1000 | 6
30 | GFM: 100
31 | GFM: 100
32 | GFM: 100
33 | GFM: 100
34 | GFM: 100
35 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
36 | GFM: 100
37 | GFM: 100
38 | GFM: 100
39 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
40 | GFM: 100
41 | GFM: 100
42 | GFM: 100
43 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
44 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
45 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
46 | GFM: 100
47 | GFM: 100
48 | GFM: 100
49 | GFM: 100
50 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
51 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
52 | GFM: 100
53 | GFM: 100
54 | GFM: 100
55 | GFM: 100
56 | GFM: 100
57 | GFM: 100
58 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
59 | 18 | 2.5 | 1.25 | 0.03 | 0.01 | 20 | 20 | 1000 | 6
60 | GFM: 100
61 | GFM: 100
62 | GFM: 100
63 | GFM: 100
64 | GFM: 100
65 | GFM: 100
66 | GFM: 100
67 | GFM: 100
68 | GFM: 100
Note on A6: Yue Zhu: Bus 1 and Bus 16 are swapt because in the Toolbox, bus 1 has to be the swing bus.
Note on B7: Yue Zhu: Synchronous machine with DC4B Exciter and a convention 3-stage PSS
Note on C18: Yue Zhu: The power rating of M1 (original M16) and M13 are 2 times of others, therefore the parameters should be changed: X becomes 1/2 of the orignal, D and H becomes 2 times.
Note on I22: Yue Zhu: deliberately detuned low.
Note on I31: Yue Zhu: Deliberately detuned high.
Note on I34: Yue Zhu: deliberately detuned low.
Note on I40: Yue Zhu: deliberately detuned low.
Note on I44: Yue Zhu: deliberately detuned low.
Note on I48: Yue Zhu: deliberately detuned low.
Note on I49: Yue Zhu: deliberately detuned low.
Note on I50: Yue Zhu: deliberately detuned low.
Note on I55: Yue Zhu: deliberately detuned low.
Note on I56: Yue Zhu: deliberately detuned low.
Note on I63: Yue Zhu: deliberately detuned low.
Note on I64: Yue Zhu: deliberately detuned low.

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 6000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
16 | 54 | 1e-07 | 0.0181 | 1e-07 | 0 | 1.025
2 | 58 | 1e-07 | 0.025 | 1e-07 | 0 | 1.07
3 | 62 | 1e-07 | 0.02 | 1e-07 | 0 | 1.07
4 | 19 | 0.0007 | 0.0142 | 1e-07 | 0 | 1.07
5 | 20 | 0.0009 | 0.018 | 1e-07 | 0 | 1.009
6 | 22 | 1e-07 | 0.0143 | 1e-07 | 0 | 1.025
7 | 23 | 0.0005 | 0.0272 | 1e-07 | 0 | 1
8 | 25 | 0.0006 | 0.0232 | 1e-07 | 0 | 1.025
9 | 29 | 0.0008 | 0.0156 | 1e-07 | 0 | 1.025
10 | 31 | 1e-07 | 0.026 | 1e-07 | 0 | 1.04
11 | 32 | 1e-07 | 0.013 | 1e-07 | 0 | 1.04
12 | 36 | 1e-07 | 0.0075 | 1e-07 | 0 | 1.04
13 | 17 | 1e-07 | 0.0033 | 1e-07 | 0 | 1.04
14 | 41 | 1e-07 | 0.0015 | 1e-07 | 0 | 1
15 | 42 | 1e-07 | 0.0015 | 1e-07 | 0 | 1
1 | 18 | 1e-07 | 0.003 | 1e-07 | 0 | 1
17 | 36 | 0.0005 | 0.0045 | 0.32 | 0 | 1
18 | 49 | 0.0076 | 0.1141 | 1.16 | 0 | 1
18 | 50 | 0.0012 | 0.0288 | 2.06 | 0 | 1
19 | 68 | 0.0016 | 0.0195 | 0.304 | 0 | 1
20 | 19 | 0.0007 | 0.0138 | 1e-07 | 0 | 1.06
21 | 68 | 0.0008 | 0.0135 | 0.2548 | 0 | 1
22 | 21 | 0.0008 | 0.014 | 0.2565 | 0 | 1
23 | 22 | 0.0006 | 0.0096 | 0.1846 | 0 | 1
24 | 23 | 0.0022 | 0.035 | 0.361 | 0 | 1
24 | 68 | 0.0003 | 0.0059 | 0.068 | 0 | 1
25 | 54 | 0.007 | 0.0086 | 0.146 | 0 | 1
26 | 25 | 0.0032 | 0.0323 | 0.531 | 0 | 1
27 | 37 | 0.0013 | 0.0173 | 0.3216 | 0 | 1
27 | 26 | 0.0014 | 0.0147 | 0.2396 | 0 | 1
28 | 26 | 0.0043 | 0.0474 | 0.7802 | 0 | 1
29 | 26 | 0.0057 | 0.0625 | 1.029 | 0 | 1
29 | 28 | 0.0014 | 0.0151 | 0.249 | 0 | 1
30 | 53 | 0.0008 | 0.0074 | 0.48 | 0 | 1
30 | 61 | 0.00095 | 0.00915 | 0.58 | 0 | 1
31 | 30 | 0.0013 | 0.0187 | 0.333 | 0 | 1
31 | 53 | 0.0016 | 0.0163 | 0.25 | 0 | 1
32 | 30 | 0.0024 | 0.0288 | 0.488 | 0 | 1
33 | 32 | 0.0008 | 0.0099 | 0.168 | 0 | 1
34 | 33 | 0.0011 | 0.0157 | 0.202 | 0 | 1
34 | 35 | 0.0001 | 0.0074 | 1e-07 | 0 | 0.946
36 | 34 | 0.0033 | 0.0111 | 1.45 | 0 | 1
36 | 61 | 0.0011 | 0.0098 | 0.68 | 0 | 1
37 | 68 | 0.0007 | 0.0089 | 0.1342 | 0 | 1
38 | 31 | 0.0011 | 0.0147 | 0.247 | 0 | 1
38 | 33 | 0.0036 | 0.0444 | 0.693 | 0 | 1
40 | 41 | 0.006 | 0.084 | 3.15 | 0 | 1
40 | 48 | 0.002 | 0.022 | 1.28 | 0 | 1
41 | 42 | 0.004 | 0.06 | 2.25 | 0 | 1
42 | 18 | 0.004 | 0.06 | 2.25 | 0 | 1
43 | 17 | 0.0005 | 0.0276 | 1e-07 | 0 | 1
44 | 39 | 1e-07 | 0.0411 | 1e-07 | 0 | 1
44 | 43 | 0.0001 | 0.0011 | 1e-07 | 0 | 1
45 | 35 | 0.0007 | 0.0175 | 1.39 | 0 | 1
45 | 39 | 1e-07 | 0.0839 | 1e-07 | 0 | 1
45 | 44 | 0.0025 | 0.073 | 1e-07 | 0 | 1
46 | 38 | 0.0022 | 0.0284 | 0.43 | 0 | 1
47 | 53 | 0.0013 | 0.0188 | 1.31 | 0 | 1
48 | 47 | 0.00125 | 0.0134 | 0.8 | 0 | 1
49 | 46 | 0.0018 | 0.0274 | 0.27 | 0 | 1
51 | 45 | 0.0004 | 0.0105 | 0.72 | 0 | 1
51 | 50 | 0.0009 | 0.0221 | 1.62 | 0 | 1
52 | 37 | 0.0007 | 0.0082 | 0.1319 | 0 | 1
52 | 55 | 0.0011 | 0.0133 | 0.2138 | 0 | 1
54 | 53 | 0.0035 | 0.0411 | 0.6987 | 0 | 1
55 | 54 | 0.0013 | 0.0151 | 0.2572 | 0 | 1
56 | 55 | 0.0013 | 0.0213 | 0.2214 | 0 | 1
57 | 56 | 0.0008 | 0.0128 | 0.1342 | 0 | 1
58 | 57 | 0.0002 | 0.0026 | 0.0434 | 0 | 1
59 | 58 | 0.0006 | 0.0092 | 0.113 | 0 | 1
60 | 57 | 0.0008 | 0.0112 | 0.1476 | 0 | 1
60 | 59 | 0.0004 | 0.0046 | 0.078 | 0 | 1
61 | 60 | 0.0023 | 0.0363 | 0.3804 | 0 | 1
63 | 58 | 0.0007 | 0.0082 | 0.1389 | 0 | 1
63 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
63 | 64 | 0.0016 | 0.0435 | 1e-07 | 0 | 1.06
65 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
65 | 64 | 0.0016 | 0.0435 | 1e-07 | 0 | 1.06
66 | 56 | 0.0008 | 0.0129 | 0.1382 | 0 | 1
66 | 65 | 0.0009 | 0.0101 | 0.1723 | 0 | 1
67 | 66 | 0.0018 | 0.0217 | 0.366 | 0 | 1
68 | 67 | 0.0009 | 0.0094 | 0.171 | 0 | 1
27 | 53 | 0.032 | 0.32 | 0.41 | 0 | 1

## Advance
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 0
Enable (plot pole map) | 1
Enable (plot admittance) | 0
Enable (print output) | 1
Enable (modal analysis) | 0