## Bus
This sheet summarizes the parameters for power flow analysis
Notes:
Area type: 1-AC, 2-DC.
AC bus type: 1-slack bus, 2-PV bus, 3-PQ bus
DC bus type: 1-slack bus (V bus), 2-NaN, 3-P bus (I bus)
The bus 1 HAVE TO be the slack bus, i.e., type-1 bus.
PGi and QGi are in generator convention. PLi and QLi are in load convention.
For active device (SG, VSI, etc), please use PGi and QGi. For load, please use PLi and QLi.
User data:
Bus No. | Bus type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1 | 0 | 40 | 0 | 0 | 0 | -999 | 999 | 1 | 1
2 | 2 | 0.98 | 0 | 5.45 | 0 | 0 | 0 | -999 | 999 | 1 | 1
3 | 2 | 0.983 | 0 | 6.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
4 | 2 | 0.997 | 0 | 6.32 | 0 | 0 | 0 | -999 | 999 | 1 | 1
5 | 2 | 1.011 | 0 | 5.05 | 0 | 0 | 0 | -999 | 999 | 1 | 1
6 | 2 | 1.05 | 0 | 7 | 0 | 0 | 0 | -999 | 999 | 1 | 1
7 | 2 | 1.063 | 0 | 5.6 | 0 | 0 | 0 | -999 | 999 | 1 | 1
8 | 2 | 1.03 | 0 | 5.4 | 0 | 0 | 0 | -999 | 999 | 1 | 1
9 | 2 | 1.025 | 0 | 8 | 0 | 0 | 0 | -999 | 999 | 1 | 1
10 | 2 | 1.01 | 0 | 5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
11 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999 | 1 | 1
12 | 2 | 1.0156 | 0 | 13.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
13 | 2 | 1.011 | 0 | 35.91 | 0 | 0 | 0 | -999 | 999 | 1 | 1
14 | 2 | 1 | 0 | 17.85 | 0 | 0 | 0 | -999 | 999 | 1 | 1
15 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999 | 1 | 1
16 | 2 | 1.045 | 0 | 2.5 | 0 | 0 | 0 | -999 | 999 | 1 | 1
17 | 3 | 1 | 0 | 0 | 0 | 60 | 3 | 0 | 0 | 1 | 1
18 | 3 | 1 | 0 | 0 | 0 | 24.7 | 1.23 | 0 | 0 | 1 | 1
19 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
20 | 3 | 1 | 0 | 0 | 0 | 6.8 | 1.03 | 0 | 0 | 1 | 1
21 | 3 | 1 | 0 | 0 | 0 | 2.74 | 1.15 | 0 | 0 | 1 | 1
22 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
23 | 3 | 1 | 0 | 0 | 0 | 2.48 | 0.85 | 0 | 0 | 1 | 1
24 | 3 | 1 | 0 | 0 | 0 | 3.09 | -0.92 | 0 | 0 | 1 | 1
25 | 3 | 1 | 0 | 0 | 0 | 2.24 | 0.47 | 0 | 0 | 1 | 1
26 | 3 | 1 | 0 | 0 | 0 | 1.39 | 0.17 | 0 | 0 | 1 | 1
27 | 3 | 1 | 0 | 0 | 0 | 2.81 | 0.76 | 0 | 0 | 1 | 1
28 | 3 | 1 | 0 | 0 | 0 | 2.06 | 0.28 | 0 | 0 | 1 | 1
29 | 3 | 1 | 0 | 0 | 0 | 2.84 | 0.27 | 0 | 0 | 1 | 1
30 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
31 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
32 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
33 | 3 | 1 | 0 | 0 | 0 | 1.12 | 0 | 0 | 0 | 1 | 1
34 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
35 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
36 | 3 | 1 | 0 | 0 | 0 | 1.02 | -0.1946 | 0 | 0 | 1 | 1
37 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
38 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
39 | 3 | 1 | 0 | 0 | 0 | 2.67 | 0.126 | 0 | 0 | 1 | 1
40 | 3 | 1 | 0 | 0 | 0 | 0.6563 | 0.2353 | 0 | 0 | 1 | 1
41 | 3 | 1 | 0 | 0 | 0 | 10 | 2.5 | 0 | 0 | 1 | 1
42 | 3 | 1 | 0 | 0 | 0 | 11.5 | 2.5 | 0 | 0 | 1 | 1
43 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
44 | 3 | 1 | 0 | 0 | 0 | 2.6755 | 0.0484 | 0 | 0 | 1 | 1
45 | 3 | 1 | 0 | 0 | 0 | 2.08 | 0.21 | 0 | 0 | 1 | 1
46 | 3 | 1 | 0 | 0 | 0 | 1.507 | 0.285 | 0 | 0 | 1 | 1
47 | 3 | 1 | 0 | 0 | 0 | 2.0312 | 0.3259 | 0 | 0 | 1 | 1
48 | 3 | 1 | 0 | 0 | 0 | 2.412 | 0.022 | 0 | 0 | 1 | 1
49 | 3 | 1 | 0 | 0 | 0 | 1.64 | 0.29 | 0 | 0 | 1 | 1
50 | 3 | 1 | 0 | 0 | 0 | 1 | -1.47 | 0 | 0 | 1 | 1
51 | 3 | 1 | 0 | 0 | 0 | 3.37 | -1.22 | 0 | 0 | 1 | 1
52 | 3 | 1 | 0 | 0 | 0 | 1.58 | 0.3 | 0 | 0 | 1 | 1
53 | 3 | 1 | 0 | 0 | 0 | 2.527 | 1.1856 | 0 | 0 | 1 | 1
54 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
55 | 3 | 1 | 0 | 0 | 0 | 3.22 | 0.02 | 0 | 0 | 1 | 1
56 | 3 | 1 | 0 | 0 | 0 | 2 | 0.736 | 0 | 0 | 1 | 1
57 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
58 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
59 | 3 | 1 | 0 | 0 | 0 | 2.34 | 0.84 | 0 | 0 | 1 | 1
60 | 3 | 1 | 0 | 0 | 0 | 2.088 | 0.708 | 0 | 0 | 1 | 1
61 | 3 | 1 | 0 | 0 | 0 | 1.04 | 1.25 | 0 | 0 | 1 | 1
62 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
63 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
64 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.88 | 0 | 0 | 1 | 1
65 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
66 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
67 | 3 | 1 | 0 | 0 | 0 | 3.2 | 1.53 | 0 | 0 | 1 | 1
68 | 3 | 1 | 0 | 0 | 0 | 3.29 | 0.32 | 0 | 0 | 1 | 1
69 | 1 | 1 | 0 | -0.5 | 0 | 0.2 | 0 | -999 | 999 | 2 | 2
70 | 3 | 1 | 0 | 0.4 | 0 | 0.2 | 0 | -999 | 999 | 2 | 2
71 | 3 | 1 | 0 | 0.3 | 0 | 0.1 | 0 | -999 | 999 | 2 | 2
72 | 3 | 1 | 0 | 0 | 0 | 0.05 | 0 | -999 | 999 | 2 | 2
73 | 3 | 1 | 0 | 0 | 0 | 0.08 | 0 | -999 | 999 | 2 | 2
74 | 3 | 1 | 0 | 0.2 | 0 | 0.2 | 0 | -999 | 999 | 2 | 2
75 | 3 | 1 | 0 | 0 | 0 | 0.15 | 0 | -999 | 999 | 2 | 2
76 | 3 | 1 | 0 | 0 | 0 | 0.02 | 0 | -999 | 999 | 2 | 2
77 | 3 | 1 | 0 | 0 | 0 | 0.01 | 0 | -999 | 999 | 2 | 2
78 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0 | -999 | 999 | 2 | 2
79 | 3 | 1 | 0 | 0 | 0 | 0.035 | 0 | -999 | 999 | 2 | 2
80 | 3 | 1 | 0 | 0 | 0 | 0.061 | 0 | -999 | 999 | 2 | 2
81 | 3 | 1 | 0 | 0 | 0 | 0.135 | 0 | -999 | 999 | 2 | 2
82 | 3 | 1 | 0 | 0 | 0 | 0.149 | 0 | -999 | 999 | 2 | 2
83 | 1 | 1 | 0 | -0.5 | 0 | 0.2 | 0 | -999 | 999 | 3 | 2
84 | 3 | 1 | 0 | 0.4 | 0 | 0.2 | 0 | -999 | 999 | 3 | 2
85 | 3 | 1 | 0 | 0.3 | 0 | 0.1 | 0 | -999 | 999 | 3 | 2
86 | 3 | 1 | 0 | 0 | 0 | 0.05 | 0 | -999 | 999 | 3 | 2
87 | 3 | 1 | 0 | 0 | 0 | 0.08 | 0 | -999 | 999 | 3 | 2
88 | 3 | 1 | 0 | 0.2 | 0 | 0.2 | 0 | -999 | 999 | 3 | 2
89 | 3 | 1 | 0 | 0 | 0 | 0.15 | 0 | -999 | 999 | 3 | 2
90 | 3 | 1 | 0 | 0 | 0 | 0.02 | 0 | -999 | 999 | 3 | 2
91 | 3 | 1 | 0 | 0 | 0 | 0.01 | 0 | -999 | 999 | 3 | 2
92 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0 | -999 | 999 | 3 | 2
93 | 3 | 1 | 0 | 0 | 0 | 0.035 | 0 | -999 | 999 | 3 | 2
94 | 3 | 1 | 0 | 0 | 0 | 0.061 | 0 | -999 | 999 | 3 | 2
95 | 3 | 1 | 0 | 0 | 0 | 0.135 | 0 | -999 | 999 | 3 | 2
96 | 3 | 1 | 0 | 0 | 0 | 0.149 | 0 | -999 | 999 | 3 | 2

## Apparatus
This sheet summarizes the apparatuses connected to buses.
User data:
Bus No. | Type | Parameters
1 | 0 | 30 | 7.5 | 0.0041 | 0.00068333
2 | 0 | 30.2 | 7.55 | 0.035 | 0.0058333
3 | 0 | 35.8 | 8.95 | 0.0304 | 0.0050667
4 | 0 | 28.6 | 7.15 | 0.0295 | 0.0049167
5 | 0 | 26 | 6.5 | 0.027 | 0.0045
6 | 0 | 34.8 | 8.7 | 0.0224 | 0.0037333
7 | 0 | 26.4 | 6.6 | 0.0322 | 0.0053667
8 | 0 | 24.3 | 6.075 | 0.028 | 0.0046667
9 | 0 | 34.5 | 8.625 | 0.0298 | 0.0049667
10 | 0 | 31 | 7.75 | 0.0199 | 0.0033167
11 | 0 | 28.2 | 7.05 | 0.0103 | 0.0017167
12 | 0 | 92.3 | 23.075 | 0.022 | 0.0036667
13 | 0 | 24 | 6 | 0.003 | 0.0005
14 | 0 | 30 | 7.5 | 0.0017 | 0.00028333
15 | 0 | 30 | 7.5 | 0.0017 | 0.00028333
16 | 0 | 42 | 10.5 | 0.0125 | 0.0020833
70 | 1010
71 | 1010
72 | 1010
75 | 1010
77 | 1010
84 | 1010
85 | 1010
86 | 1010
89 | 1010
91 | 1010
39,69 | 2001 |  |  |  |  | 60 | 20 | 10
55,83 | 2001 |  |  |  |  | 40 | 30 | 20

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Notes:
In this form, a pi-circuit between two buses, i.e., series R+jX impedance with parallel G/2+jB/2 admittance at two terminals.
The transformer is added between FromBus and branch.
The branches can be listed in arbitrary order.
FromBus should NOT equal to ToBus in this list.
For using this sheet, please set enable from 0 to 1, then this sheet will over-write "NetworkLine"
Enable:
1
User data:
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio
16 | 54 | 1e-07 | 0.0181 | 0 | 0 | 1.025
2 | 58 | 1e-07 | 0.025 | 0 | 0 | 1.07
3 | 62 | 1e-07 | 0.02 | 0 | 0 | 1.07
4 | 19 | 0.0007 | 0.0142 | 0 | 0 | 1.07
5 | 20 | 0.0009 | 0.018 | 0 | 0 | 1.009
6 | 22 | 1e-07 | 0.0143 | 0 | 0 | 1.025
7 | 23 | 0.0005 | 0.0272 | 0 | 0 | 1
8 | 25 | 0.0006 | 0.0232 | 0 | 0 | 1.025
9 | 29 | 0.0008 | 0.0156 | 0 | 0 | 1.025
10 | 31 | 1e-07 | 0.026 | 0 | 0 | 1.04
11 | 32 | 1e-07 | 0.013 | 0 | 0 | 1.04
12 | 36 | 1e-07 | 0.0075 | 0 | 0 | 1.04
13 | 17 | 1e-07 | 0.0033 | 0 | 0 | 1.04
14 | 41 | 1e-07 | 0.0015 | 0 | 0 | 1
15 | 42 | 1e-07 | 0.0015 | 0 | 0 | 1
1 | 18 | 1e-07 | 0.003 | 0 | 0 | 1
17 | 36 | 0.0005 | 0.0045 | 0.32 | 0 | 1
18 | 49 | 0.0076 | 0.1141 | 1.16 | 0 | 1
18 | 50 | 0.0012 | 0.0288 | 2.06 | 0 | 1
19 | 68 | 0.0016 | 0.0195 | 0.304 | 0 | 1
20 | 19 | 0.0007 | 0.0138 | 0 | 0 | 1.06
21 | 68 | 0.0008 | 0.0135 | 0.2548 | 0 | 1
22 | 21 | 0.0008 | 0.014 | 0.2565 | 0 | 1
23 | 22 | 0.0006 | 0.0096 | 0.1846 | 0 | 1
24 | 23 | 0.0022 | 0.035 | 0.361 | 0 | 1
24 | 68 | 0.0003 | 0.0059 | 0.068 | 0 | 1
25 | 54 | 0.007 | 0.0086 | 0.146 | 0 | 1
26 | 25 | 0.0032 | 0.0323 | 0.531 | 0 | 1
27 | 37 | 0.0013 | 0.0173 | 0.3216 | 0 | 1
27 | 26 | 0.0014 | 0.0147 | 0.2396 | 0 | 1
28 | 26 | 0.0043 | 0.0474 | 0.7802 | 0 | 1
29 | 26 | 0.0057 | 0.0625 | 1.029 | 0 | 1
29 | 28 | 0.0014 | 0.0151 | 0.249 | 0 | 1
30 | 53 | 0.0008 | 0.0074 | 0.48 | 0 | 1
30 | 61 | 0.00095 | 0.00915 | 0.58 | 0 | 1
31 | 30 | 0.0013 | 0.0187 | 0.333 | 0 | 1
31 | 53 | 0.0016 | 0.0163 | 0.25 | 0 | 1
32 | 30 | 0.0024 | 0.0288 | 0.488 | 0 | 1
33 | 32 | 0.0008 | 0.0099 | 0.168 | 0 | 1
34 | 33 | 0.0011 | 0.0157 | 0.202 | 0 | 1
34 | 35 | 0.0001 | 0.0074 | 0 | 0 | 0.946
36 | 34 | 0.0033 | 0.0111 | 1.45 | 0 | 1
36 | 61 | 0.0011 | 0.0098 | 0.68 | 0 | 1
37 | 68 | 0.0007 | 0.0089 | 0.1342 | 0 | 1
38 | 31 | 0.0011 | 0.0147 | 0.247 | 0 | 1
38 | 33 | 0.0036 | 0.0444 | 0.693 | 0 | 1
40 | 41 | 0.006 | 0.084 | 3.15 | 0 | 1
40 | 48 | 0.002 | 0.022 | 1.28 | 0 | 1
41 | 42 | 0.004 | 0.06 | 2.25 | 0 | 1
42 | 18 | 0.004 | 0.06 | 2.25 | 0 | 1
43 | 17 | 0.0005 | 0.0276 | 0 | 0 | 1
44 | 39 | 1e-07 | 0.0411 | 0 | 0 | 1
44 | 43 | 0.0001 | 0.0011 | 0 | 0 | 1
45 | 35 | 0.0007 | 0.0175 | 1.39 | 0 | 1
45 | 39 | 1e-07 | 0.0839 | 0 | 0 | 1
45 | 44 | 0.0025 | 0.073 | 0 | 0 | 1
46 | 38 | 0.0022 | 0.0284 | 0.43 | 0 | 1
47 | 53 | 0.0013 | 0.0188 | 1.31 | 0 | 1
48 | 47 | 0.00125 | 0.0134 | 0.8 | 0 | 1
49 | 46 | 0.0018 | 0.0274 | 0.27 | 0 | 1
51 | 45 | 0.0004 | 0.0105 | 0.72 | 0 | 1
51 | 50 | 0.0009 | 0.0221 | 1.62 | 0 | 1
52 | 37 | 0.0007 | 0.0082 | 0.1319 | 0 | 1
52 | 55 | 0.0011 | 0.0133 | 0.2138 | 0 | 1
54 | 53 | 0.0035 | 0.0411 | 0.6987 | 0 | 1
55 | 54 | 0.0013 | 0.0151 | 0.2572 | 0 | 1
56 | 55 | 0.0013 | 0.0213 | 0.2214 | 0 | 1
57 | 56 | 0.0008 | 0.0128 | 0.1342 | 0 | 1
58 | 57 | 0.0002 | 0.0026 | 0.0434 | 0 | 1
59 | 58 | 0.0006 | 0.0092 | 0.113 | 0 | 1
60 | 57 | 0.0008 | 0.0112 | 0.1476 | 0 | 1
60 | 59 | 0.0004 | 0.0046 | 0.078 | 0 | 1
61 | 60 | 0.0023 | 0.0363 | 0.3804 | 0 | 1
63 | 58 | 0.0007 | 0.0082 | 0.1389 | 0 | 1
63 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
63 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
65 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
65 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
66 | 56 | 0.0008 | 0.0129 | 0.1382 | 0 | 1
66 | 65 | 0.0009 | 0.0101 | 0.1723 | 0 | 1
67 | 66 | 0.0018 | 0.0217 | 0.366 | 0 | 1
68 | 67 | 0.0009 | 0.0094 | 0.171 | 0 | 1
27 | 53 | 0.032 | 0.32 | 0.41 | 0 | 1
69 | 70 | 0.01938 | 0.05917 | 0 | 0 | 1
69 | 73 | 0.05403 | 0.22304 | 0 | 0 | 1
70 | 71 | 0.04699 | 0.19797 | 0 | 0 | 1
70 | 72 | 0.05811 | 0.17632 | 0 | 0 | 1
70 | 73 | 0.05695 | 0.17388 | 0 | 0 | 1
71 | 72 | 0.06701 | 0.17103 | 0 | 0 | 1
72 | 73 | 0.01335 | 0.04211 | 0 | 0 | 1
72 | 75 | 0.02 | 0.20912 | 0 | 0 | 1
73 | 74 | 0.03 | 0.3 | 0 | 0 | 1
73 | 76 | 0.03 | 0.3 | 0 | 0 | 1
74 | 77 | 0.03 | 0.3 | 0 | 0 | 1
74 | 78 | 0.03 | 0.3 | 0 | 0 | 1
74 | 79 | 0.03 | 0.3 | 0 | 0 | 1
75 | 80 | 0.03 | 0.3 | 0 | 0 | 1
75 | 81 | 0.03 | 0.3 | 0 | 0 | 1
75 | 82 | 0.03 | 0.3 | 0 | 0 | 1
83 | 84 | 0.01938 | 0.05917 | 0 | 0 | 1
83 | 87 | 0.05403 | 0.22304 | 0 | 0 | 1
84 | 85 | 0.04699 | 0.19797 | 0 | 0 | 1
84 | 86 | 0.05811 | 0.17632 | 0 | 0 | 1
84 | 87 | 0.05695 | 0.17388 | 0 | 0 | 1
85 | 86 | 0.06701 | 0.17103 | 0 | 0 | 1
86 | 87 | 0.01335 | 0.04211 | 0 | 0 | 1
86 | 89 | 0.02 | 0.20912 | 0 | 0 | 1
87 | 88 | 0.03 | 0.3 | 0 | 0 | 1
87 | 90 | 0.03 | 0.3 | 0 | 0 | 1
88 | 91 | 0.03 | 0.3 | 0 | 0 | 1
88 | 92 | 0.03 | 0.3 | 0 | 0 | 1
88 | 93 | 0.03 | 0.3 | 0 | 0 | 1
89 | 94 | 0.03 | 0.3 | 0 | 0 | 1
89 | 95 | 0.03 | 0.3 | 0 | 0 | 1
89 | 96 | 0.03 | 0.3 | 0 | 0 | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
Notes:
In this form, Zbranch = R+jwL+1/(G+jwC)
The transformer is added by turn ratio, which is connected between FromBus and Zbranch in the layout.
The branches can be listed in arbitrary order.
Mutual branch HAS TO be RL.
Self branch HAS TO be GC.
User data:
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## Basic
This sheet summarizes basic settings
User data:
Samping frequency (Hz) | 30000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## Advance
This sheet summaries advanced settings.
User data:
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 1
Enable (create simulink model) | 0
Enable (plot pole map) | 0
Enable (plot admittance) | 0
Enable (print output) | 0
Enable (participation) | 0